## Slide 1: Security Constrained Optimal Power Flow PowerModelsACDCsecurityconstrained.jl
Ghulam Mohy ud din
Early Research Career Fellow

## Slide 2: Outline
Security Constrained AC-DC Optimal Power Flow (SCOPF)
Exact Formulation
Soft Formulation
Robust Formulation
Test Case 67 node AC-DC Power System
Results - Exact Formulation

## Slide 3: Optimal Power Flow (OPF)

## Slide 4: Key Point in OPF

## Slide 5: Security Constrained Optimal Power Flow (SCOPF)
According to “Power System Security Guidelines and System Strength Requirements Methodology ” from AEMO:
Power Networks are regulated to be “N-1 Secure”
Intention, the network can withstand the spontaneous failure of any single component during daily operations
Details in practice
Focus on a specific subset of component failures
Many constraints can be exceeded for a short amount of time
What is the time scale? (1s, vs 1 min, 5min)
Available recourse actions?

## Slide 6: The Core Challenge of Security Constraints
 How to solve the base case OPF problem subject to the contingency cases?

## Slide 7: Stochastic Programming (SP)

## Slide 8: Two Stage – Two Period SP
Multi period
Single period
Second stage
First stage

## Slide 9: Two Stage – Two Period SP

## Slide 10: Two-Stage SCOPF
Single period
Multi period

## Slide 11: Contingency Filters
Base Case
(ACDC OPF)
Sets of Contingencies by Ranks
Contingency Cuts
(ACDC PF)
Initial Operating Point
Violations
Rank the generator, branch, and branchdc contingencies and down selects based on evaluation limits
Check a given operating point against the contingencies to look for violations. The unbounded ACDC Power Flow is used for the simulation
Return a list of contingencies where a violation is found

## Slide 12: Corrective and Preventive SCOPF (PSCOPF)
In a correctively secure system, any post-contingency constraint violation can be removed by suitable remedial actions
In a preventive secure system, without any remedial action, none of the probable contingencies causes constraint violation, The results clearly indicate the system operation state can be changed from a given operation point to a PSCOPF satisfied operation point by exerting beforehand control actions in specified number

## Slide 13: ACDC SCOPF Algorithm
Base Case
(ACDC OPF)
Set of Contingencies
Base Case
Contingency 1 Case
Contingency n Case
ACDC-SCOPF (Multiperiod ACDCOPF with Response Constraints)
(ACDC PF)
Initial Operating Point
Contingencies Filter
Violations
Solution
Iterations

## Slide 14: First-Stage Formulation (AC-DC OPF)

## Slide 15: First-Stage Formulation (OPF)
Variables:
Subject to:
, , , , , , , , ,
Node Voltage
DC Branch Flow
Power Flow Converter Transformer

## Slide 16: First-Stage Formulation (OPF)
Filter Reactive Power
Nodal balance B/w filter, phase reactor, xformer
Converter Active /Reactive Power
Converter DC side Power
Converter loss model
Converter AC side Current and Voltage

## Slide 17: First-Stage Formulation (OPF)
Converter DC side Current and Voltage
Firing angle of Thyristors for LCC converters
DC Power Balance

## Slide 18: Second-Stage Formulation
Similar to first-stage feasibility set
Response constraints “link” to the first stage decisions
dc_grid_constraints(.)
dc_grid_variables

## Slide 19: Second Stage Generator Active Power Response

## Slide 20: Second Stage Generator Reactive Power Response
 Further relaxations (SOC, SDP, LP) are adopted from PowerModels.jl & powerModelsACDC.jl

## Slide 21: SCOPF – Soft Formulation – First-Stage
dc_grid_constraints(.)
dc_grid_variables
dc grid constraint slacks

## Slide 22: SCOPF – Soft Formulation – Second-Stage
dc_grid_variables
dc_grid_constraints(.)
 Plenty of variations (PTDF, Linear Cuts) possible, working on the algorithm!

## Slide 23: SCOPF – Robust Formulation
A bilevel max-min optimization model is proposed to find the worst contingency scenario while solving an ac optimal power flow problem considering corrective actions.
The overall objective is to minimize the total cost including generation and load shedding cost while satisfying all relevant constraints in the worst contingency scenario.
The upper-level problem allows representing contingencies (N-1 or N-2) using binary variables and maximizes the violations.
The lower-level problem solves ac optimal power flow problem considering corrective actions and minimizes the total cost.
This model can be solved using SOC approximations and duality theory.
 Next formulation to work on!

## Slide 24: Benchmark Test Case
AC Grid
DC Grid
Grid Data:
AC Nodes: 67
AC Branches: 102
Transformers: 26
Converters: 9
HVDC Nodes: 9
HVDC Branches: 11
Syn Generators: 17
Wind Generators: 3
Contingencies:
AC Contingencies: 11
HVDC Contingencies: 2

## Slide 25: Results: Base Case

## Slide 26: Results: Base Case

## Slide 27: Results: Base Case

## Slide 28: Results: Base Case

## Slide 29: Results: Base Case

## Slide 30: Results: Base Case

## Slide 31: Results: Base Case

## Slide 32: Results: Contingencies
C1

## Slide 33: Results: Contingencies
C2

## Slide 34: Results: Contingencies
C3

## Slide 35: Results: Contingencies
C4

## Slide 36: Results: Contingencies
C5

## Slide 37: Results: Contingencies
C6

## Slide 38: Results: Contingencies
C7

## Slide 39: Results: Contingencies
C8

## Slide 40: Results: Contingencies
C9

## Slide 41: Results: Contingencies
C10

## Slide 42: Results: Contingencies
C11

## Slide 43: Results: Contingencies
C12

## Slide 44: Results: Contingencies
C13

## Slide 45: Results: Final Solution

## Slide 46: Results: Final Solution

## Slide 47: Results: Final Solution

## Slide 48: Results: Final Solution

## Slide 49: Results: Final Solution

## Slide 50: Results: Final Solution

## Slide 51: Results: Final Solution

## Slide 52: Results: Cost and Losses
Base Case Cost: 65008.85599
Base Case losses: 38.34147224609092
Final Case Cost: 65096.57699
Final Case losses: 43.4649814388526

## Slide 53: Thank You
Thank you for your attention!
Dr. Ghulam Mohy Ud Din
Ghulam Mohy Ud Din E:moh050@csiro.au